[image: image3.png]


Fluid Control Research Institute, Kanjikode West, Palakkad
Tender Document – Supply, Installation, Commissioning & Testing of New VFD for 187kW Pump-Motor including Removal of old Panel, etc.

TENDER DOCUMENT

 SUPPLY, INSTALLATION, COMMISSIONING & TESTING OF VFD FOR 187KW PUMP-MOTOR 
	FLUID CONTROL RESEARCH INSTITUTE

KANJIKODE WEST – 678 623, PALAKKAD, KERALA

(Under Ministry of Heavy Industries & Public Enterprises – Govt. of India)

Phone: (91) 491-2566120 / 2566206 / 2569009 Fax: 2566326

E-mail: purchase@fcriindia.com, fcri@vsnl.com
Website: http://www.fcriindia.com



VOLUME I OF III
TECHNICAL SPECIFICATIONS OF 
 VFD 
Last Date for Submission of the Tender: 30/10/2020
CONTENTS

	Sl No.
	Description
	Page No.

	I
	Scope 
	4-7

	II
	Other features & requirements  
	7

	III
	Data with the Offer
	7

	IV
	Inspection & Testing
	8

	V
	Package & Marking
	8

	VI
	Guarantee
	8

	VII
	Technical Checklist
	9

	VIII
	Bidder Technical Questionnaire 


	10

	IX
	Technical Deviations
	11

	X
	Similar Orders Executed
	12


Technical Specifications:
I. Scope of work
Supply, installation, testing and commissioning of VFD Drive for 250HP Pump Motor under buyback of the existing Delta Drive VFD with its panel. 

Quantity required: 1 Set

The VFD shall be supplied with prewired ready to install Panel, fully equipped with input and output harmonic suppression filters, filters for overvoltage protection (dv/dt), built in provisions for minimization of capacitor leakage current between phases and phase to ground.

VFD shall be with following specifications:

· Load: 3 phase Induction Motor, 440V 50Hz

· Motor Load: 187 kW (nominal)

· VFD Output frequency Range: 0 to 120/150Hz.

· VFD shall be configured for max 50 Hz at rated speed of motor. 
· Input filters like EMC/EMI filters for reducing the high frequency electromagnetic noise as per EN 61800-3 environments 2 category C3
· Input fuses, Active front end drive with LCL filter and contactor and DC Bus Capacitors at the input side for harmonic reduction. THD shall be equal to or less than 5% as per IEEE 519-1992/2014 and EN 50160

· Filters for overvoltage protection and to minimize the capacitive leakage current between phases and phases to ground (dv/dt filters) at the output side of the drive

· Built-in RTC clock, Event logging, built-in control (PI function)

· Removable Terminal blocks

· Near unity True power factor at Full load

· Analog Inputs: 4 to 20mA

· VFD Construction shall be with built-in heat sink and cooling system for operation at ambient temperature range 10 to 50 deg. C and humidity from 40% to 100% RH.

· MTBF: Exceeding 25 years is desirable

· Easy to Use User Interface with keypad and Display with RJ45 style connector

· Display for Alarms & Errors.

· Protective features built-in including:
Heat sink over temperature, phase-to-phase and ground-fault short circuit protection, Over / under torque protection, Over / under voltage protection

· Drive efficiency: 96 to 98%

· Displacement power factor: 0.98

· Frequency resolution: 0.01 Hz

· Communication ports: MODBUS/RTU

· The VFD is to be supplied with software for monitoring the operations status as well as Operating remotely for Speed Control & ON/OFF. The scope of supply also includes appropriate Data Interface module for remote operation and configurations over RS485 or Ethernet. The location of PC is about 35 metres or more from the VFD. The cable work from VFD to PC is in scope of FCRI. The PC for installation of software is in scope of FCRI.

· Warranty: 2 Years or more. (VFD + Panel)
VFD Panel:

The VFD and its harmonic suppression filter set are to be installed within the Panel.

Panel shall be made of steel sheet of thickness 2mm (minimum) and with minimum dimensions 2200 x 950 x 600 mm or similar greater dimensions (as per standard). The Panel height shall be suitable for the location 2.35 metre height (Ceiling / beam height from floor at VFD Panel location) in the room with proper clearance at all sides of Panel as per CEA standards, powder coated both on inside and outside and with provisions for incomer and outgoing power cables of size (typically) 3C x 240 Sq.mm AYFY Cable 4 numbers. Suitable Beading, Door Handles and Lock/Key for secure access, Cooling Fans with Filters, Panel internal light with door switch, etc. shall be provided.

Panel shall be supplied with Analog Controls for Speed, Digital Indication for % Speed for Pump-motor, Indicator lamps for error on trip, ON/OFF controls, Emergency TRIP push-button, etc. Panel shall also have R-Y-B power status Indicator lamps.

Panel shall protect the VFD for the ambient operating conditions Temperature 45 deg.C (peak summer) and 100% RH (Humidity during monsoon). Hence Panel shall have appropriate weather protection, Ingress Protection and Cooling arrangement. The VFD shall be suited to operate in the said conditions without Failure. Hence both VFD and Panel shall be of suitable Construction with built-in heat sink and cooling system for operation at ambient temperature range 10 to 50 deg. C and humidity from 40% to 100% RH.

The present panel to motor cable length (approx. after adding 10 m free length) is about 50 metres. 
Name Plate Detail of pump motor: 
Machine No. NADZ 92011DV (MTG.V1)

KW/HP: 187/251
            Volt: 415+/-10% 
            RPM: 1490

A: 303Δ


EFF (FL): 95.5%

DUTY: S1

HZ: 50+/- 5%

             IP 55


            FRAME: ND315L

AMB: 45°C

             REF: AFAM1247
            BRGS DE/NDE 6319-3/6319-C3

RELUB HRS: 5000/5000
 CONN DIA: 302

INS. CL.: F

Details of Existing Delta Drive VFD: (AS is Where Is Condition/ For Buy-back)

Model: VFD1850B43W

Input: 3Ph 380-480V 50/60Hz 380A

Output: 3Ph 0-480V 370A 281KVA 250HP

Frequency range: 0.1-120Hz

Enclosure: Type 1
Existing Panel Size: 220 x 95 x 60 cm (AS is Where Is Condition/ For Buy-back)
Electromagnetic Compatibility
Conducted radio-frequency immunity test level 3 conforming to IEC 61000-4-6
Electrical fast transient/burst immunity test level 4 conforming to IEC 61000-4-4
Electrostatic discharge immunity test level 3 conforming to IEC 61000-4-2
Radiated radio-frequency electromagnetic field immunity test level 3 conforming to IEC 61000-4-3
Voltage dips and interruptions immunity test conforming to IEC 61000-4-11

Protections to be incorporated: 

· Against exceeding limit speed: drive

· Against input phase loss: drive

· Break on the control circuit: drive

· Input phase breaks: drive

· Line supply over-voltage: drive

· Line supply under-voltage: drive

· Overcurrent between output phases and earth: drive

· Overheating protection: drive

· Over-voltages on the DC bus: drive

· Power removal: drive

· Short-circuit between motor phases: drive

· Thermal protection: drive

· Motor phase break: motor

· Power removal: motor

· Thermal protection: motor

Recommended Standard practices for Electromagnetic Emission control: To be followed in Design and Manufacture of the Panels, Cabling / Wiring internal to panel, Cabling Terminations, etc.
Conducted emission

Conducted disturbances can propagate to other equipment via all conductive parts including cabling, earthing and the metal frame of an enclosure

Conductive emissions can be reduced in the following way:

– By RFI filtering for HF disturbances

– Using ferrite rings in power connection points

– Using an AC or DC choke (even meant against harmonics, it reduce HF disturbances as well.

– Using an LCL filter in the case of regenerative drives

– Using a du/dt filter

Radiated emission 

To be able to effectively prevent disturbance through the air, all parts of the power drive system should form a Faraday cage against radiated emissions. The installation of a PDS includes cabinets, auxiliary boxes, cabling, motors, etc.

 Some methods for ensuring the continuity of the Faraday cage are listed as follows: 

Panel Enclosure

Unpainted metal-to-metal contacts shall be used throughout, with conductive gaskets, where appropriate.

Use unpainted installation plates, bonded to a common earth point, ensuring all separate metal items are firmly bonded to achieve a single path to earth.

Use conductive gaskets in doors and covers. Separate the radiative i.e, “dirty” side from the “clean side” by metal covers and design.

Holes in enclosure should be minimized. 

Cabling and wiring

– Use conductive gaskets for HF earthing of control cable shield.

– Use shielded control cables. 

– Allow no breaks in the cable shields.

– Select shield connections with low impedance on the MHz range.

– Route power and control cables separately. 

– Use twisted pairs to avoid disturbances. 

– Use ferrite rings for disturbances, where necessary.

– Select and route internal wires correctly.

Installation

– Auxiliaries used with complete drive modules (CDMs) should be CE marked products conforming to both the EMC & Low Voltage Directives.

– Selection and installation of accessories in accordance with manufacturers’ instructions.

– For cabinet models, lead the cables into the inside of the enclosure. Apply 360° grounding of the cable shield at the entry into the cabinet. 

Scope of work includes cable terminations. The existing cable runs from VFD Panel to Motor and the incomer to VFD are to be used. All termination works at VFD panel are in scope of Contractor. 

II. Other features & requirements:
     1. Warranty details to be provided.

     2. Details of maintenance support to be provided.

III. Data with the offer

     Supplier shall submit following data with the bid. 
     1. List of deviation from the above specifications.

     2. Detailed specification sheets.
     3. Manufacture’s complete descriptive and illustrative catalogue/literature 
 Incase of failure to submit the documents listed above, the offer may be rejected without any information.
 1.  All documents shall be English
 2.  Final documents are to be submitted in CD
IV.   Inspection and Testing 
    1. FCRI reserves the right to test and inspect the item at the vendor’s works  

        In line with inspection test plan.

    2.  If the witness inspection is not carried out by FCRI the tests shall be    

         completed by the vendor and documents for the same submitted for   

        scrutiny.

    3. Acceptance will be subject to satisfactory performance of the items during 

         the test at FCRI.
V. Package & Marking
Packing shall be done in a manner to reduce the volume of package.
Detailed packing list in waterproof envelope shall be inserted in the package together with equipment.

Items shall be marked as per relevant standards if required as applicable.
Items shall be suitably protected to avoid any damage during transit and storage.
VI. Guarantee
Supplier shall guarantee that the instrument comply with the requirements stated in the requisition and in the purchase order. Supplier shall replace or repair all parts found to be defective due to inadequate engineering or quality of material. Supplier shall replace the instrument without delay, if the defect or malfunctioning cannot be eliminated.

Any defects occurring within the time period specified shall be repaired making all necessary modifications/repair/replacement of defective parts free of charge to FCRI.
VII. Technical Check List (As applicabl.

	Sl.No.
	Description 
	Response  Yes/No

	1
	GA Drawing  with dimension and details of equipment /Material 
	

	2
	Bill of material 
	

	3
	Technical literature 
	

	4
	Data Sheets
	

	5
	Materials as per data sheets and specifications
	

	6
	Sign & Stamp of the tender, data sheets, drawings etc.
	

	7
	Contents/Index page number for attached documents/drawings/certificate
	

	8
	Submitted filed technical questionnaire
	

	9
	Details of manufacture inspection, venue details of setup, facility at works.
	

	10
	Make of the various items as per the approved vendor
	

	11
	Items and vendor list for approval of FCRI for the items
	

	12
	Estimated shipping weight & volume of each item 
	


                                                                                           Name & Désignation 
Place : 

                                                                                            Authorised Signature 

Date : 

                                                       Office Seal 
VIII.      Bidder Technical Questionnaire (As applicable)



Bidder shall fill in and submit along with unpriced bid document. 

	Sl No.
	Description
	Vendor Confirmation

Yes/No/NA

	1
	Deviation 

a. Job specifications

b. Equipment specifications as per data sheets 

c. Scope of supply as material requisition 
If Yes include the list of deviations. 
	

	2
	List of commissioning spares
	

	3
	Relevant technical catalogues in English with model decoding details, drawings etc.
	

	4
	Customer reference list in India and abroad.
	



Note: -

              If the response is ‘NO’, please enclose reasons 



Name & Designation
Place:
 







 

Date: 






Authorized Signature  


Office Seal

IX. Technical Deviations:

1. Deviation 

  List of deviations from requisition/specifications/standards/drawings.

	Sl.No
	Documents
	Deviation 



	
	No. Title 
	Clause 
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


2. No Deviation is required

Place :                                                                               Name & Designation 

Date : 

                                                                                         Authorized  Signature 

                                                             Office Seal 
X. Similar Orders Executed
	Sl.No.
	Description 
	Name  & Postal Address 
	Phone 
	Value of order 
	Delivery  data as per Contract
	Actual Delivery Date 

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	  
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


Note :  Copies of procurement order/completion certificate for the above supply to be enclosed.  Later 5 years need to be indicated here.

Place :                                                                                    Name & Designation 

Date : 

                                                                                              Authorized Signature  

                                                           Office Seal 
VOLUME II OF III
GENERAL CONDITIONS
CONTENTS

	  Sl. No.
           

	Description
	Pages



	1
	Bidders Eligibility Criteria
	             15

	2
	General Information to Tenders
	16


	3
	Instructions to Tenders
	17


	4
	Tender Notice
	18


	5
	Format - Letter of Authority
	             19


	6
7.

8.            
	Format for Bank Guarantee EMD                                         

Format for Bank Guarantee SD                                                      

Form for Contract cum Performance Bank Guarantee

	20
21
             22


	9.


	Details of Indian Agent
	24


	10
	Commercial Check List
	25


	11
	Scope of Contract
	26


	12
	General Rules and Directions for Guidance
	35


	13
	Award of Contract
	42


	14
	Preambles


	43


     15        Bank Details                                                                                44
I. Bidders Eligibility Criteria:

1.
Invitation for Bids is open to bidders who qualify the eligibility criteria. 

2.
The bidder should have executed at least one job of similar nature either in India or abroad in the preceding 3 years reckoned from bid due date. 
3.
The bidder shall not have been declared as ineligible by FCRI for corrupt or fraudulent practices as defined in ITB. 

4.
Bid should be from original manufacturers. Bids from selling agents / authorized distributors/ authorized dealers/ will be considered, provided bids are supplied with authority letter from the concerned manufacturers valid at the time of bidding. Warranty cover will be provided by such bidder.  

II. General Information To Tenderers

Name of the Institution

:  M/s. Fluid Control Research Institute, Kanjikode West

Name of work

            : Supply, Installation, Commissioning & Testing of New VFD for 
                                         187kW Pump- Motor including Removal of old Panel.
Tender reference        
             :  PUR/FCRI/20046/VFD/2020-2021                                                                                        
Cost of Tender Form

:  Rs.100.00
EMD (Rs)


:  Rs.10000.00 
EMD (USD)


:  
Due date for submission
:  30/10/2020
Signature of the tenderer
: 

Name



:

Designation


:

Address



:

Date



:

Place



: 
III. Instructions to Tenderers

1. 
The following three documents constitute the complete tender specifications

· Technical Tender Specification 

· Tender Document – General Conditions
· Price Schedule 

2. 
Full signatures are required in the following:

a) 
Index Page 

b) 
Tender Form 

c) 
Price Schedule 

3. 
Initials are required in all other pages including preambles.

4. 
The rates should be quoted in words also.

5. 
The conditions of tender ought to be read carefully.

6. 
The tender should be submitted in two (2) parts in separate sealed envelope superscribing the tender reference, name of work, due date and nature of bid (priced or unpriced).

7.   UAM Number should be provided by the MSME Bidders. 

Part I – The Unpriced Bid

a) Tender documents duly completed along with unpriced schedule of quantities, all technical and commercial details.

b) List of deviations / modifications or variations, if any, to the specifications and terms & conditions.

c) Profile of the Firm / Company.

d) An affidavit stating, “None of the supply/works carried out by me were not cancelled owing to my fault”.

e) All necessary documents mentioned in Scope of Contract (X) & General Rules (XI)

f) All necessary items mentioned in Volume – I 

g) EMD by way of RTGS/NEFT in favour of Fluid Control Research Institute, payable at Palakkad  or Bank Guarantee in INR issued by a Public Sector Bank in FCRI format.
h) Tender fee by way of RTGS/NEFT in favour of Fluid Control Research Institute, . 
Part II – The priced bid

One set of the schedule of quantities and rates duly signed on all pages

(To be submitted in the Priced Bid format).

The Tender fee and EMD should be submitted by RTGS/NEFT before submission of quotation, the receipt of RTGS/NEFT should be attached along with the technical bid. If the EMD is by Bank Guarantee, the same should be attached along with the technical bid.
IV. Tender Notice

To

Dear Sir,
Sub:


1. Sealed item rate tenders are invited from reputed manufacturers/ suppliers/ exclusive Indian agents for the following work intended vide technical tender enclosed 

2. The following documents have been enclosed:

a) Technical tender specification 

b) Tender document – General Conditions
c) Price Schedule 

3. The un-priced bids will be opened and evaluated by FCRI authorities. The priced bids will be opened at FCRI in presence of the qualified tenderers or a single authorized representative of the tenderer. The exact date of opening will be informed later.

4. No consideration will be given to any tender received after due time and date.

5. After finalization of the purchase, an amount of @10% of the total tendered value must be deposited by the successful tenderer as ‘Security Deposit’ for the due fulfillment of the contract, before releasing the purchase order. The Security Deposit will be returned to the successful supplier after receipt of material at FCRI.  Security Deposit should be submitted within 10 days from the date of receipt of Scanned copy of Procurement order. Delivery period will be counted from the date of receipt of scanned copy of Procurement order.
The Earnest Money will be retained as a part of the Security Deposit and balance amount must be deposited by the way of RTGS/NEFT in favour of Fluid Control Research 
Institute. or by Bank Guarantee in INR, from a Public Sector Bank in FCRI format.
6. The security deposit will bear no interest. 

7. The tenderer will submit his tender after carefully examining all the Tender Documents.

8. The tender shall be valid for acceptance for a minimum period of SIX MONTHS from the date of its opening.


Place: 

Name & Designation 


Date:





Authorized Signature  


Office Seal
V.
Letter of Authority for Attending Price Bid Opening and Subsequent Negotiations.










Date:

Fluid Control Research Institute, 

Kanjikode West, Palakkad,

Kerala, India – 678 623

Dear Sir, 
Sub: 

Bid No.…………………….……for …………………………………………………………………………….
M/s …………………………………………. hereby authorize following personnel to attend the price bid opening and for subsequent discussions/registration/correspondence and communication against above Bid. 
1. Name & Designation …………………………………………… Signature ………………………………..
2. Name & Designation ………………………………………….. Signature ………………………………..
We confirm that we shall be bound by all commitments made by aforementioned authorized representatives. 
Tanking you
Yours faithfully, 
Place: 






Name & Designation

Date: 
















Authorized Signature






Office Seal

Note: - 


This letter of authority should be on bidder’s letterhead and should be signed by a person 
competent having the power of attorney to bind the bidder. 


Not more than two persons are permitted to attend techno–commercial 
negotiations/pricebid opening. 
VI. 
Form for Bank Guarantee for Earnest Money Deposit 

(To be issued by a Public Sector Bank)

(Stamp in accordance with the Stamp Act)

Ref............... 





           Bank Guarantee No.........

Date......................

To,

Fluid Control Research Institute 

Kanjikode West, Palakkad, 

Kerala, India – 678623 

Dear Sir(s),

TENDER NO._______________ 
FOR_________________________________

WHEREAS.....................................................(hereinafter called the Bidder has submitted his Bid no. …………………. Dated……......for ..............................(hereinafter called 'the bid')

KNOW ALL MEN by these presents that WE.........................………………………… are bound unto Fluid Control Research Institute (An autonomous body under Govt. of India, Ministry of Heavy Industries & Public Enterprises), Kanjikode West, Palakkad, Kerala, India – 678623 (herein after called FCRI) IN THE SUM OF...………………………for which payment well and truly to be made to FCRI, the Bank binds itself its successor and assigns by these presents. Sealed with the Common Seal of the Bank this... day of... 

THE CONDITIONS OF THIS OBLIGATION ARE:

1. If the Bidder withdraws his Bid during the period of Bid validity specified by the Bidder on the Bid Form ; or

2. If the Bidder, having been notified of the acceptance of his bid by FCRI during the period of bid validity but

a) Fails or refuses to execute the Contract Form, if required; or

b) Fails or refuses to furnish the PERFORMANCE SECURITY in accordance with the instructions to bidder.

We undertake to pay FCRI upto the above amount upon receipt of its first written demand, without FCRI having to substantiate its demand, provided that in its demand FCRI will note that the amount claimed by it is due to it owing to the occurrence of one or both of the two conditions specifying the occurred condition or conditions.

The Guarantee will remain in force upto _____________and any demand in respect thereof should reach the BANK not later than the above date.

(Signature of the BANK)

Signature of the Witness

Name & Address of Witness:





Date:
VII. 
Form for Bank Guarantee for Security Deposit

(To be issued by a Public Sector Bank in INR)

(Stamp in accordance with the Stamp Act)

Ref............... 





Bank Guarantee No.........

Date......................

To,

Fluid Control Research Institute 

Kanjikode West, Palakkad, 

Kerala, India – 678623 

Dear Sir(s),

TENDER NO._______________ 
FOR_________________________________

PURCHASE ORDER NO. __________________________________dt_____________

WHEREAS..................................................... (hereinafter called the Bidder has submitted his Bid no. …………………. Dated……......for .............................. (hereinafter called 'the bid')

KNOW ALL MEN by these presents that WE.........................………………………… are bound unto Fluid Control Research Institute (An autonomous body under Govt. of India, Ministry of Heavy Industries & Public Enterprises), Kanjikode West, Palakkad, Kerala, India – 678623 (herein after called FCRI) IN THE SUM OF...………………………for which payment well and truly to be made to FCRI, the Bank binds itself its successor and assigns by these presents. Sealed with the Common Seal of the Bank this... day of... 

THE CONDITIONS OF THIS OBLIGATION ARE :

3. If the Bidder fails to perform as per the above mentioned Purchase Order; or

4. If the Bidder, having been notified of the acceptance of his bid by FCRI during the period of bid validity but

a) Fails or refuses to execute the Contract Form, if required; or

b) Fails or refuses to furnish the PERFORMANCE SECURITY in accordance with the instructions to bidder.

We undertake to pay FCRI upto the above amount upon receipt of its first written demand, without FCRI having to substantiate its demand, provided that in its demand FCRI will note that the amount claimed by it is due to it owing to the occurrence of one or both of the two conditions specifying the occurred condition or conditions.

The Guarantee will remain in force upto _____________and any demand in respect thereof should reach the BANK not later than the above date.

(Signature of the BANK)

Signature of the Witness

Name & Address of Witness:





Date
                         VIII.         Performance Bank Guarantee

(To be issued by a Public Sector  Bank in INR
(Stamp in accordance with the Stamp Act)
To: 

M/s. Fluid Control Research Institute
Kanjikode West, Palakkad – 678 623
Kerala
THIS DEED OF GUARANTEE executed by ………………………………………….. registered under the Nationalised Bank, constituted under the Banking Companies (Acquisition and Transfer of Undertakings), Act, having its registered office at …..………..…………………………………….. and one of its branch at ………………………...……………………….………………. (Hereinafter referred to as “the Bank”) in favour of M/s. Fluid Control Research Institute, an autonomous R&D organisation registered under the Societies Registration Act, 1860 and having its office at Kanjikode West, Palakkad, Kerala (hereinafter referred to as “FCRI”) for an amount of not exceeding Rs……………… (Rupees……………….……….………………………….. only) at the request of M/s………… .………… …………… ……… …… ……… …… ……… …… …… … … …… …………...

This guarantee is issued subject to the condition that the liability of the Bank under this Guarantee is limited to a maximum of Rs…………………… (Rupees.….….……… …………………………………………….. only) and the guarantee shall remain in full force upto …………..(date of expiry) and cannot be invoked otherwise than by a written demand or claim under the guarantee served on the Bank on or before the …………………….. [Last date of claim(after completion of one month from the date of expiry of the BG)].
Whereas the Fluid Control Research Institute has placed a purchase order No. …………… ……………………….………………… (Called the Order) with M/s…… …..…… …………… .… ….….……………… (Hereinafter referred to as the Contractor/Supplier) for ………….…………………………………….. (Name of work/supply) (Hereinafter referred to as the Work/Supply)  for FCRI and whereas it is one  of the conditions of the order that the Contractor/Supplier shall submit a Performance Bank Guarantee of10% of the total order value, 10% of the order value being Rs…………… (Rupees ……………………………………………………………….………….. only).
We ………………………….. ……. hereby undertake that we will pay to the FCRI without any demur, merely on a demand from the FCRI any sum or sums which may from time  to time demanded by the FCRI upto maximum of Rs….……..….. (Rupees……… …………….…………………………………………….………. only)
We …..…………………….. do hereby undertake to pay the amount demanded under this guarantee without any demur, merely on a  demand  from  the FCRI.  Any such demand made on the bank shall be conclusive as regards the amount due and payable by the Bank under this guarantee.
We undertake to pay to the FCRI any money so demanded notwithstanding any dispute or disputes raised by the Contractor/Supplier in any suit or proceeding pending before any  court or Tribunal relating  thereto  our liability under this present being absolute and unequivocal.
The payment so made by us under this guarantee shall be a valid discharge of our liability for payment there under and the said Contractor/Supplier shall have no claim against us for making such payment.
We ………………….. further agree that the guarantee herein contained shall remain in full force until (a) payment has been made to the FCRI by the Bank of the aggregate amount payable hereunder or (b) all the items of Work/Supply as per the order has been completed in accordance with the conditions of the order or till the expiry of this guarantee and the FCRI discharges the guarantee accordingly whichever shall first occur.
We, ….………………….………… further agree with the FCRI that they shall have the fullest liberty without consent and without affecting in any manner our obligations hereunder grant time or other indulgence to or compound with the Contractor/Supplier or enter into any agreement or composition or agree to forebear to enforce any of the terms and conditions of the said order, against the Contractor/Supplier or agree to vary any of the terms and conditions of the said order or by any such matter or thing which under the law relating to sureties but for this provision have the effect of so relieving us.
This guarantee shall not be affected by any change in the constitution of the bank or the FCRI of the Contractor/Supplier nor shall this guarantee be affected by any change in the constitution of the FCRI or said Contractor/Supplier by absorption with any other body or corporation and this guarantee shall be available to or enforceable by such body or corporation.
Our guarantee shall remain in force until ……………..…. unless a claim or demand is made within one month after the expiry of the above date, all the FCRI’s right under the guarantee shall be deemed as waived/forfeited and we shall be relieved and discharged from all liabilities there under.
We …………………………………………..… lastly undertake not to revoke this guarantee during its currency except with the previous consent of the FCRI in writing.
Notwithstanding anything to the contrary contained herein.
a.
Our liability under this Bank Guarantee shall not exceed of Rs………………. (Rupees……………………………….………………………… only).

b.
This Bank Guarantee shall be valid upto ……………………..

c.
We are liable to pay the guaranteed amount or any part thereof under this bank guarantee if and  only if you serve upon us a written claim or demand on or before ……………………..…..(Last date of claim)

Place:
Date:
IX 
Details of Indian Agent /Consultant/ Representative

To

Fluid Control Research Institute, 

Kanjikode West, Palakkad,

Kerala, India – 678 623

1 Name of Indian agent/ Consultant/ 


Representative



: 

2 Address




:




3 Nature of Services to be rendered

:

4 Name of Contract Person


:

1. Telephone Number



:

2. Fax Number

3. E-mail address & Web Site


:

4. PAN NO.

5. Agency commission included in 

 


quoted prices as % of quoted FOB


prices (payable in equivalent Indian 


rupees upon receipt of acceptance 


of items at site) 



: % In  Figures and Words

a. Relationship (Whether Agent /

Consultant/ Representative/ Retainer

/ Associates)



: 

11 
Account No. In Any SBI/HDFC/ICICI 


Branch which having E-Banking 


Facilities of Indian Agent 


: 

12 Branch Code and Account Code 

: 

(Payment towards IAC shall be released through e-banking only)

Note: 
Copy of agreement between principal and agent to be enclosed with 




the bid.

Place: 







Authorized Signature 




Date: 







Name and Designation 






Office Seal



X. Commercial Check List

	Sl No.
	Description
	Response Yes/No

	1
	BEC Documentary Evidence


	

	2
	Priced Bid (In separate sealed envelop)

	

	3
	Un priced bid (In separate sealed envelop)

	

	4
	Complete commercial terms and conditions along with un-priced bid

	

	5
	Delivery Period To be indicated in un-priced bid. 

	

	6
	Bid validity To be indicated in the  un-priced bid.

	

	7
	EMD by DD/Cash/BG from a Public Sector Bank in INR in FCRI format. 

	

	8
	Tender Cost by DD/Cash To be attached along with un-priced bid

	

	
	
	

	
	
	


XI. Scope of Contract

1. 
General 

1
Scope of contract shall be as defined in the Purchase Order and Technical Specifications, Drawings and Annexure. 

2
Completeness of the equipment shall be the responsibility of the supplier. Any accessories not specifically mentioned in the specifications, but necessary for the satisfactory functioning of the equipment shall be provided by supplier without any extra cost.

3.
Supplier shall follow the best modern practices in the manufacture of equipment notwithstanding any omission in the specifications. The true intent and meaning of these documents is that supplier in all respects, design, engineering, manufacture and supply of the equipment in a thorough manner and supply the same within time to the entire satisfaction of FCRI.

4.
Supplier shall furnish 2 (two) copies of Technical documents, final drawings, preservation instructions, operation and maintenance manuals, test certificates, spare parts catalogues for all equipments etc. in English to Fluid Control Research Institute. 

5.
Documents once submitted shall be firm and final and not subject to subsequent changes. Supplier shall be responsible for any loss to FCRI consequent to furnishing of incorrect data/drawings.

6.
All dimensions and weight should be in metric system.

7.
All equipment to be supplied and work to be carried out shall conform to and comply with the provisions of relevant regulations/Acts as may be applicable to the type of equipment/work carried out and necessary certificates shall be furnished.

8. 
Supplier shall provide cross sectional drawings, wherever applicable, to identify the spare part numbers and their location. The size of bearings, their make and number shall be furnished, if applicable. 

9.
Specifications, design and drawings issued to the supplier are not soled or given but loaned. They remain property of FCRI. Supplier and his employees shall not make use of the drawings, specifications and technical information for any purpose at any time except for manufacture against and shall not disclose the same to any person, firm or corporate body.

10.
Supplier shall pack, protect, mark and dispatch equipment as per instructions given in the contract.

2. 
Standards

Equipment supplied under the CONTRACT shall conform to the standards mentioned in the Technical Specifications, or such other standards which ensure equal or higher quality.
3.
Use of Contract Documents 


Supplier shall not, disclose the Contract or any provision thereof, or any specification, plan, drawing, pattern, sample or information furnished therewith, to any person other than a person employed by the supplier in the performance of the Contract. Disclosure to any such person shall be made in confidence and shall extend only so far as may be necessary for purpose of such performance. 

4. Modification 

1.
Modifications with respect to technical and/or commercial aspects including terms of delivery shall be considered valid only when accepted in writing by FCRI. 

2.
FCRI shall not be bound by any printed conditions or provisions in the supplier’s Bid Forms or acknowledgment of Contract, invoices, packing list and other documents which purport to impose any conditions at variance with or supplemental to Contract.

5.
Patent Rights, Liability & Compliance of Regulations

1.
Supplier hereby warrants that the use of equipment will not infringe claims of any patent and supplier agrees to be responsible for and to defend at his sole expense all suits and proceedings against FCRI based on any such alleged patent infringement and to pay all costs, expenses and damages which FCRI may have to pay or incur by reason of any such suit or proceedings. 

2.
Supplier shall indemnify FCRI against all third party claims of infringement of patent, trademark or industrial design rights arising from use of the equipment

Supplier shall also protect and fully indemnify FCRI from any claims from supplier’s discretion for any acts of commissions or omission while executing the Contract.

Supplier shall be responsible for compliance and shall protect and indemnify completely FCRI from any claims/penalties arising out of any infringements.
6.
Inspection & Testing 

1.
FCRI shall have the right to inspect and/or to test the Equipment for conformity to specifications. 

2.
Inspections and tests may be conducted at supplier premises. Facilities and assistance including access to the drawings and production data shall be furnished to the inspectors at no charge. 


3.
FCRI may reject any inspected or tested equipment fail to conform to the specifications 
and supplier shall either replace or make necessary alterations to meet specifications 
requirements at free of cost. 
4.
FCRI has right to inspect, test and reject the equipment after the equipment arrival at FCRI. It will not be limited or waived by reason of the equipment having previously been inspected, tested and passed by FCRI, or their representative prior to the equipment shipment. 

5.
FCRI shall follow the progress of the manufacture of the equipment to ensure that the requirements are not being deviated with respect to schedule and quality.

6.
Supplier shall allow FCRI to visit, during working hours, the workshops relevant for execution during the entire period of validity.

7.
In order to enable FCRI’s representatives to obtain entry visas in time, SUPPLIER shall notify FCRI two months before assembly, testing and packing of main equipment. If requested, supplier shall assist FCRI’s representatives in getting visas in the shortest possible time (applicable only in case of foreign order).

8.
Supplier shall place at the disposal of FCRI, free of charge, with all tools, instruments, and other apparatus necessary for the inspection and/or testing of the equipment. FCRI is entitled to prohibit the use and dispatch of equipment and/or materials, which have failed to comply with the characteristics required for the equipment during tests and inspections.

9.
Supplier shall advise in writing of any delay in the inspection schedule with reasons for delay and the proposed corrective action.

10.
All tests and trials in general, including those to be carried out for materials not manufactured by supplier shall be witnessed by FCRI. Therefore, supplier shall confirm to FCRI by fax or e-mail about the exact date of inspection with at least 30 days notice. Supplier shall specify the equipment and quantities ready for testing and indicate whether a preliminary or final test is to be carried out.
11.
FCRI should waive the right to witness the test; timely necessary information will be given accordingly.

12.
Any and all expenses incurred in connection with tests, preparation of reports and analysis made by qualified laboratories, necessary technical documents, testing documents and drawings shall be at supplier’s cost. The technical documents shall include the reference and numbers of the standards used and wherever deemed practical by FCRI, copy of such standards.

13.
Arrangements for all inspections required by Indian Statutory Authorities and as specified in technical specifications shall be made by supplier.

7.
Rejection of Equipment 
1.
When equipments/materials are rejected, the supplier shall be intimated with the details of such rejected equipments/materials, reasons, and location. Supplier shall remove the item or give instructions as to dispose within 15 days. In the case of dangerous, infected and perishable materials within 48 hours, failing which FCRI will either return the materials to the contractor freight to pay or otherwise dispose at the contractor’s risk and cost. FCRI shall be entitled to recover handling and storage charges for the period of not removed, @ 5% of the values of materials for each month or part of a month till the rejected materials are finally disposed off. 

2.
Inspection at supplier’s works by FCRI shall not prejudice FCRI’s claim for rejection of the equipment on final inspection at FCRI

3.
If equipments are not of specification or fail to perform specified duties, FCRI shall reject the equipment and ask free replacement at supplier’s cost and risk. 

4.
Equipment rejected shall be removed by the Supplier at his cost within 15 days of notice after repaying the amounts received against the supply. FCRI shall in no way be responsible for any deterioration or damage to the equipment under any circumstances whatsoever.

5.
In case of rejection, FCRI shall have the right to recover the amounts, if any, from any of invoices. 

8.
Time Schedule

1.
Supplier shall submit to FCRI, his time schedule regarding documentation, manufacture, testing, supply, erection and commissioning of the Equipment. 

2.
The time schedule shall be in the form of network/a bar chart clearly indicating all main or key events as above.

3.
FCRI shall have the right to inspect supplier’s premises a view to evaluate the actual progress of work on the basis of supplier’s time schedule documentation.

4.
Supplier shall advise FCRI, at the earliest possible date of any anticipated delay in progress.


5.
In case progress at various stages are not as per phased time schedule and are not satisfactory. FCRI may give notice of the same in writing to the supplier to make good the failure, neglect or contravention. Should supplier fail to comply with such notice FCRI shall have the option and be at liberty to take the contract wholly or in part out of the supplier’s hand and make alternative arrangements to obtain the requirements and completion of contract at the supplier’s risk and cost and recover from the supplier all extra cost incurred by FCRI on this account. In such event FCRI shall not be responsible for any loss, supplier may incur and shall not be entitled to any gain. FCRI shall, in addition, have the right to encash Performance Guarantee in full or part.

9.
Delivery

1.
Delivery of the equipment shall be made by the supplier in accordance with terms and shall remain at the risk of the supplier until delivery has been completed.

2.
Delivery shall be deemed to have been made,

a) In case of FOB, CFR & CIF, when the Equipments have been put on board the Ship/Aircraft and a clean Bill of Lading/Airway Bill are obtained. 

b) In case of FOT site (for Indian bidders) on receipt of Equipment by FCRI.

3.
Delivery terms are binding and essential and consequently, no delay is allowed without the written approval of FCRI. Any request concerning delay will be void unless accepted by FCRI. 

4.
Delivery time shall include time for submission of drawings for approval, incorporation of comments, if any, and final approval of drawings by FCRI. It shall be deemed to be the essence of the contract. 

10
Transportation

1.
Where the supplier is required to deliver the equipment FOB, transport of the equipment shall be arranged and paid for by the SUPPLIER and the cost thereof shall be included in the bid.

2.
Where the supplier is required to deliver the equipment CFR or CIF, transport of the Equipment shall be arranged and paid for by the supplier and the cost shall be included in the bid.

11
Incidental Services 

1.
Supplier shall furnish tools for assembly and maintenance for performance/supervision and start-up of equipment.  

2.
Furnishing tools for assembly and/or maintenance. 

3.
Performance/supervision/maintenance/repair of the supplied Equipment, for a period time agreed, provided that this service shall not relieve the supplier of any warrantee/guarantee obligations under the contract.

4.
Training of FCRI’s personnel at the supplier’s plant and/or at site, in assembly, start-up operation, maintenance and/or repair at no extra cost. However, FCRI will bear boarding, lodging & personal expenses of trainees.
5.
Supplier shall depute necessary personnel for supervision and/or erection of the Equipment at site for duration to be specified by FCRI on mutually agreed terms. 

6.
Supplier’s personnel shall be available at site within seven days for emergency action and twenty-one days for medium and long-term assistance, from the date of notice given by FCRI.

7.
Cost of applicable incidental services shall be shown separately in the price schedules.
12
Spare Parts and Accessories 

1.
Supplier shall furnish a list of recommended spares and accessories for the equipment required during start-up and commissioning. Supplier shall furnish a list of recommended spares and accessories, if required during the warranty period. Supplier shall quote for spares & accessories as per Material Requisition. 

2.
In the event of termination of production of the spare parts:

i) Advance notification to FCRI of the pending termination, in sufficient time to permit FCRI to procure needed requirements, and

ii) Following such termination, furnishing at no cost to FCRI, the blue prints, drawings and specifications of the spare parts, if any when requested.

3.
Supplier shall supply item wise list with value of spare parts and maintenance tools requirements, along with full details of manufacturer/vendor for such spares/maintenance tools.

4.
Spare parts shall be new and of first class quality as per engineering standards/ codes free of any defects deficiency in design, materials and workmanship and also shall be completely interchangeable with the corresponding parts.

5.
Type and sizes of bearings shall be clearly indicated.

6.
Spare parts shall be packed for long storage under tropical climatic conditions in suitable cases, clearly marked as to intended purpose.

7.
A list of special tools required for normal maintenance and special handling and lifting appliances, if any, for the Equipment shall be submitted to FCRI.

13
Insurance

1.
Equipment shall be fully insured in a freely convertible currency against loss or damage incidental to manufacture or acquisition, transportation, storage and delivery.

2.
Where delivery is on FOB or CFR basis, marine insurance shall be the responsibility of FCRI.

Insurance Requirements: 


Indigenous Bidders
: 
Transit risk insurance shall be arranged and borne by FCRI. 

      Foreign Bidders
      :  
Marine insurance as well as transit insurance in India shall be 



           

arranged and borne by FCRI. 

14
Guarantee

1. Supplier shall be supply the Equipment or Materials strictly in accordance with the specifications, drawings, data sheets, other attachments and conditions. No deviation from such specifications or alterations or of these conditions shall be made without written permission of FCRI, which must be obtained before any work. Equipment, irrespective of whether engineering, design data or other information has been furnished, reviewed or approved by FCRI/shall be guaranteed to be of the best quality and shall be free from faulty design, workmanship and materials, and to be of sufficient size and capacity and of proper materials so as to fulfill in all respects all operating conditions, 

2.
Supplier shall make alterations, repairs and replacements for any trouble or defect originating with the design, material, workmanship or operating characteristics of any materials arises at any time prior to twelve (12) months form the date of the commissioning or twenty four (24) months from the date of last shipment whichever period shall first expire, at his own expense and as promptly as possible. It may necessary to permit the materials to function in accordance with the specifications and to fulfill the forgoing guarantees. Supplier shall be guarantee for repaired or replaced materials/items for a period of not less than twelve (12) months from the date of repair/ replacement. In the event that the materials supplied do not meet the specifications and/or not in accordance with the drawings data sheets or the terms of the Contract and rectification is required at site, FCRI shall notify the SUPPLIER giving full details of differences. The supplier shall attend the site within seven (7) days of receipt of such notice to meet and agree with representatives of FCRI, the action required to correct the deficiency. Should the supplier fail to attend, FCRI shall immediately rectify the work/materials and supplier shall reimburse to FCRI all costs and expenses incurred in connection with such trouble or defect.

3.
Supplier shall guarantee that the performance of the equipment shall be in conformity with the specifications and shall perform the specified duties. 

4.
If the supplier fails, he shall investigate the causes and carry out necessary rectifications/modifications to achieve the guaranteed performance. In case the supplier fails to do he shall replace the equipment and prove guaranteed performance of the new equipment without any extra cost.

5.
If the supplier fails to prove the guarantee, FCRI shall take over the equipment and rectify, if possible, to fulfill the guarantee. All expenditure incurred by FCRI shall be to supplier’s account.

15
Subletting & Assignment


The contractor shall not without previous consent in writing of FCRI authority, sublet, transfer or assign the contract or any part thereof or interest therein or benefit or advantage thereof in any manner whatsoever. Provided, nevertheless, that any such consent shall not relieve the contractor from any obligation, duty or responsibility under the contract. 
16
Termination 

1.
If the supplier fails to deliver the equipment within the time specified, If the supplier fails to perform any other obligation and If the supplier does not cure his failure within a period of 30 days after receipt of the default notice, FCRI may terminate the contract in whole or in part. 

2.
FCRI shall procure equipment similar to those undelivered and the supplier shall be liable to FCRI for any excess costs. However, supplier shall continue performance of the contract to the extent not terminated.

3.
In case of termination of contract, FCRI shall not be issued any type of enquiry to the party for three years from the date of termination. 

4.
Termination for Insolvency FCRI may at any time, terminate the contract by giving written notice to the supplier, without compensation to the supplier, if the supplier becomes bankrupt or otherwise insolvent, that such termination will not prejudice or affect any right of action or remedy which has accrued or will accrue thereafter to FCRI.
17
Force Majeure

1.
Force Majeure shall be limited to

a) War/hostilities

b) Riot or Civil commotion

c) Earthquake, flood, tempest, lightening or other natural physical disaster.

d) Restrictions imposed by the Government or other statutory bodies 

2.   Supplier shall inform FCRI duly certified by the local chamber of commerce or       

      statutory authorities, causes of delay within seven days of the occurrence and cessation 

      of such Force Majeure Conditions. FCRI reserves the right to cancel the contract 

      if the delay lasting over one month. 

3.
Supplier shall specify the extent of Force Majeure Conditions prevalent in their works at the time of submitting their bid and shall take into consideration in bid. In the event of Force Majeure cause, the supplier or FCRI shall not be liable for delays in performing their obligations and delaying period will be extended. 

18
Resolution of Disputes/Arbitration

1.
FCRI and supplier shall make every effort to resolve amicably by direct negotiations any disagreement or dispute 

2.
If FCRI and the supplier have been unable to resolve amicably within thirty days, either party may require that the dispute be referred for resolution to the formal mechanism. 

3.
The Contract shall be construed and operated as an Indian Contract in accordance with Indian Laws as in force for the time being and is subject to and referred to Indian Court.
19
Arbitration

1.
All disputes, controversies, or claims between the parties, where the decision of the Engineer-in-Charge is deemed to be final and binding, which cannot be mutually resolved time shall be referred to Arbitration. FCRI shall suggest a panel of three independent and distinguished persons to select one to act as the sole Arbitrator. In the event of failure of the Supplier to select within 30 days, FCRI shall have discretion to proceed with the appointment of the Sole Arbitrator. The award of the Sole Arbitrator shall be final and binding on the parties and unless directed/awarded otherwise by the Sole Arbitrator, the cost of arbitration proceedings shall be shared equally by the parties. 

2.
The arbitration proceeding shall be in English and the venue shall be at Palakkad, Kerala India. Subject to the exclusive jurisdiction of the Courts situated in the State of Kerala, India. 

3.
The work shall continue during the Arbitration proceedings and no payment shall be withheld during arbitration. 
20
Notices

1.
Any notice given by one party to the other shall be sent by email and confirmed by fax. 

2.
A notice shall be effective when delivered or it’s effective date, whichever is later.

21
Taxes & Duties

1. Foreign Supplier is entirely responsible for taxes, stamp duties, license fees, and other such levies imposed in foreign country.
2. Indian supplier shall be entirely responsible for all taxes, licence fees etc. incurred until the delivery of equipment to FCRI. 
3. As per Govt. notification No. 45/2017-Central Tax (Rate) dt. 14-11-2017, GST @ 5% only is payable by FCRI against GST Exemption Certificate. You are requested to forward the quotation accordingly.
4. FCRI is permitted for claiming Customs Duty exemption through our duty free passbook, on Equipment/Spare parts/Accessories and Consumables imported, with reference to Govt. Notification No.  51/96-Customs dated 23rd July 1996. 

5. Income tax payable for services rendered by supplier shall be as per the Indian Income Tax Act and shall be borne by supplier. Bidder/supplier shall ascertain the amount of these taxes and to include them in bid price.

22
Books & Records

1.
Supplier shall maintain adequate records and shall make them available for inspection and audit by FCRI or their authorized agents or representatives during the terms of Contract until expiry of the performance guarantee. 

23
Permits & Certificates

1.
Supplier shall procure all necessary permits, certificates and licenses required by virtue of all applicable laws, regulations, ordinances and other rules in effect at the place where any of the work is to be performed, and supplier agrees to hold FCRI harmless from liability or penalty which might be imposed by reason of any asserted or established violation of such laws, regulations, ordinances or other rules. 
2. Mill test certificates relevant to chemical analysis and mechanical properties of the materials used for equipment construction as per the relevant standards. 

3. Test certificates on hydrostatic and pneumatic tests in case of valves and actuators 

4. Test reports on radiograph and ultrasonic inspection.

5. Test report on operation of equipment conforming to specification.

6. Test reports and certificates as required by API 6D and this specification. 
The certificates shall be valid only when signed by FCRI and certified equipments shall be dispatched to FCRI.  
24
General

1.
Losses due to non-compliance of Instructions:

Losses or damages occurring to FCRI owing to the supplier’s failure to adhere to any of the instructions shall be recoverable from the supplier.

2.
All costs, damages or expenses which FCRI may have paid, for which supplier is liable, may be recovered by FCRI from any money due to or becoming due to the SUPPLIER under this Contract. If the same due to the SUPPLIER be not sufficient to recover the recoverable amount, the SUPPLIER shall pay to FCRI, on demand, the balance amount. 

3.
No sum paid by FCRI nor any extension of the date for completion granted by FCRI shall affect or prejudice the rights of FCRI against the supplier or relieve the supplier of his obligation for the due fulfillment of CONTRACT.

4.
No claims or correspondence shall be entertained by FCRI after 90 days after expiry of performance guarantee 

25
Fall Clause 

1.
Price charged for equipment/materials supplied under the order shall in no event exceed the lowest price at which the supplier or his agent/principal/dealer sells the equipments/materials of identical description to any organization/department of the Central Govt./Dept. Of a State Govt./Statutory Undertaking of the Central/State Govt. as the case may be, during the currency of the order.

2.
If the supplier/agent/principal/dealer reduces the sale price, he shall notify such reduction the FCRI.

3.
Supplier shall furnish the following certificate to FCRI along with each bill for payment for supplies made against this order:- “We certify that there has been no reduction in sale price of the items/Equipment/materials of description identical to those supplied to FCRI under the order herein and such items/Equipment/materials have not been offered/sold at a price lower than the price charged to FCRI under the order”. 

26
Publicity & Advertising

1.
Supplier shall not make a reference to FCRI or any Company affiliated with FCRI or to the destination or the description of Equipment or services supplied under the contract in any publication, publicity or advertising media without the written permission of FCRI.
27
Re-order

1. FCRI reserves the right to repeat order upto 50% of the total order value without any change in unit price or other terms and conditions within 6 months of first order. 

28
Limitation of Liability

1. Total liability of supplier under the Agreement shall be limited to 100% of Agreement / Order price. However, neither party shall be liable to the other party for any indirect and consequential damages, loss of profits or loss of production.

XII. General Rules and Directions for Guidance

1. Bid Submission 

1.
Tenders shall be submitted in sealed covers superscribing the Tender Number and name of the work due date and nature of bid (priced or unpriced), and addressed legibly to officer inviting the tender. Full name and address of the tenderer should be written on the envelope as well as on the tender below the signature.

2. All the pages of the tender documents and any other enclosures submitted by the tenderer must properly signed or initialed and dated on each page, and also signed and dated at the places mentioned in the documents by the tenderer or such person or persons on his behalf as are legally authorized or required to sign for the tenderer. The tenderer shall in particular satisfy the Institute that he is competent and authorized to submit the tender and to enter into a legally binding contract with the Institute on behalf of himself, his firm, Company or Corporation as the case may be. A person signing the tender or any document forming part of the tender on behalf of another shall be deemed to warrant that he has the requisite authority of sign for other, and if, on enquiry, it appears that the person so signing has no authority to do so, the Institute may, without prejudice to any other Civil and Criminal remedies, cancel the contract and hold the signatory liable for all costs and damages.

3. Schedule of quantities and rates should be carefully and properly filled in. All rates should be indicated in words as well as in figures. Erasures and alterations in the tender documents should be avoided. If any corrections are necessary the original entry should be scored off and new entry legibly made duly attested by the full signature of the tenderer with date. Failure to do so may cause rejection of the tender by the Institute at its discretion. Any statement and/or letters signed separately and issued to the Institute either before or after the tender may not be considered.

4. In case of firms, all partners of the firm or such person or persons as may be legally competent to sign for the firm should sign the tender documents. In case of company, the official seal of the company should be affixed in the tender documents and should be signed by such person(s) as may be authorized by the articles of Association of the Company to sign for and on behalf of the Company. A copy of the Articles of Association should be sent with the tender. In any case, the tenderer should disclose his constitution and copies of all necessary legal documents in support thereof such as the duly registered partnership deed in the case of partnership firm should be produced as and when called for by the Institute.

5. Each tenderer shall submit a declaration as to whether he is an individual, firm or Association of firms, Company or Corporation and has the requisite organization including technical and other personnel and financial and other resources to handle the work. Full information, supported by documentary evidence shall be furnished by the tenderer in regard to the following among other things so as to demonstrate his ability to undertake the work as specified.

a)
In the case of firm, company or corporation

i. The legal name, the nature of business and the date and place of registration (including the state of incorporation where it is a corporation).

ii. The authorized, subscribed and paid up capital.

iii. The names and addresses of all the Directors including those of the Chief Executive Officer, President, Secretary or the person authorized to bind the firm, company or corporation in the matter.
b)
Tenderer shall include the names and addresses of all the partners in case of partnership.

c)
If the tenderer is an association of firms, the details of all participating firms shall be shown in tender.

d)
In the case of Indian Agent of a Foreign Organization, percentage of commission payable to Indian Agent, copy of agency agreement with Foreign Organization and certificate of enlistment with DGS&D under compulsory registration scheme of Ministry of Finance.

The Institute will be the sole judge as to the merits of the tender’s ability to perform the work. Non-submission of documentary evidence of any of the aforementioned aspects may render the tender liable to summary rejection. 

6. Total amount of tender should be written in the same language that the tender signed. 

7. The specified amount of Earnest Money must be deposited either by NEFT/RTGS 
or Bank Guarantee. If the EMD by Bank Guarantee, the same should be enclosed with the Technical Bid.   Cheque/Demad Draft will not be accepted.
8. The Earnest Money of the successful tenderer will be retained towards ‘Security Deposit’ and in the case of others, will be returned on application after finalization of the purchase.

9. The Earnest Money shall be liable to be forfeited without prejudice to the other rights and remedies of the Institute in the event of the tenderer failing (a) to keep his tender valid and open for acceptance by the Institute for and during the period of six months reckoned from the date of opening of tenders; or (b) to furnish, the requisite documents, etc. within the specified time. 

10. The Security Deposit shall liable to be forfeited without prejudice to the other rights and remedies of the Institute if the successful tenderer is failing to accept the purchase order placed by the Institute, within 15 days of its issue. The Institute shall also have the right to forfeit the Security Deposit in case the suppliers fail to execute the order as per the terms & conditions of the order. 

11. Should the tenderer have relative or relatives, or in the case of a firm or company or contractors, one or more of its shareholders employed in any capacity in the Institute, the tenderer should furnish complete information to that effect at the time of submission of the tender.

12. Tenders which do not fulfill all or any of the above conditions or incomplete in any respect are liable to be rejected.

13. The right of accepting any tender or rejecting any or all tenders without assigning any reason is reserved.

14. Tenderer should be enclosed Sales tax and Income tax clearance certificates along with the tender.

15 FCRI has standard payment terms (ie) 100% payment will be made within 45 days from the date of receipt of the material at FCRI, installation & commissioning and also in producing a Bank Guarantee for 10% of the value as performance guarantee valid for 12 months from the date of commissioning or 18 months from the date of supply whichever is earlier.. The PBG should be submitted in Indian Rupees, in our format, from a Public Sector Bank.
16.
Tenderer can notify FCRI in writing or by faxing or by email for any clarification on documents. FCRI will respond in writing to any request for clarification on bidding documents within 5 days prior to the deadline for the submission of bids.  FCRI’s response will be sent to all prospective bidders who have downloaded bidding documents.

17. At any time prior to the bid due date, FCRI may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective bidder, modify the bidding documents, by issuing addenda. 

Any addendum thus issued shall be part of the Bidding Documents pursuant to ITB Clause-5.1 and shall be notified in writing by fax/post to all prospective bidders. Prospective bidders shall promptly acknowledge receipt of each addendum by post, fax and email to FCRI. 

18
I shall extend the bid due date in order to allow prospective bidders, a reasonable time to furnish their most competitive bid considering the amendments issued. 

2 
Documentation  

Documentation shall be delivered in due time, in proper form and in the required number of copies as specified, in English.

Vendor shall submit the following documents during the submission of bid:

In pursuant to ITB Clause 9, the bidder shall furnish, as a part of the bid, document establishing the eligibility and conformity to the bidding documents of all equipment and services, which the bidder proposes to supply under the Contract. 

Description of the essential technical and performance characteristics of the Equipment and a clause-by-clause commentary on FCRI’S Technical specifications demonstrating the Equipment and services’ substantial responsiveness to the specifications. 

General arrangement / assembly drawings showing all features and relative positions and sizes of vents, gear operator / actuator, painting, coating and other external parts together with overall dimensions. 

Sectional drawing showing major parts with reference numbers and material specification and a blow-up drawing of ball-seat assembly shall be furnished complying the requirement of this specification. 

For purpose of the commentary the bidder shall note that standards for workmanship, material and equipment, and reference to brand names or catalogue numbers, designated by FCRI in its Technical Specifications are intended to be descriptive only and not restrictive. 

The drawings to be submitted shall be in total compliance with the requirement of technical specification and data sheets of equipment with no exception & deviation.

Detailed sectional arrangement drawings showing all parts with reference numbers and material specifications as referred above. 

Assembly drawings with overall dimensions and features. Complete dimensional details of support foot (where applicable) shall be indicated in these drawings as referred applied on the equipment. 

Manufacture of equipment shall commence only after approval of the above documents. Once the purchaser has given the approval, any changes in design, material and method of Manufacturer shall be notified to FCRI whose approval in writing of all changes shall be obtained before the item is manufactured. 
3. Withdrawal and Modification of Tender 

Bidder can modify or withdraw his bid after the bid submission, but before the due date of submission provided that the written notice of the modification, including substitution or withdrawal of the bid is received by FCRI prior to the due date for submission of bids. 

Bidder’s modification or withdrawal notice shall be prepared, sealed, marked and delivered in accordance with the provisions of ITB Clause-20, with the envelopes marked “modification” or “withdrawal” as appropriate. A withdrawal notice may also be sent by fax/post, but followed by a signed confirmation copy post marked not later than due date for submission of bids. 

No bid shall be modified after the due date for submission of bids. 

No bid shall be allowed to be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified by the bidder on the Bid Form. Withdrawal of a bid during this interval shall result in the bidder’s forfeiture of his bid security. 

4. Process Confidentially 

Information relating to the examination, clarifications, evaluation and comparison of bids and recommendations for the order, will not be disclosed to bidders or any other person officially concerned with. FCRI requires that Bidders/Suppliers observe the highest standard of ethics during the procurement and execution of the order. In pursuance of this policy, FCRI defines for the purposes of this provision
5. Contacting FCRI 

From the time of the bid opening to the time of the release of order, if any bidder wishes to contact FCRI for any matter relating to the bid, he should do so in writing. 

6. Conversion To Single Currency 

To facilitate evaluation and comparison, FCRI will convert all bid prices expressed in the amounts in various currencies to Indian Rupees at the bills selling exchange rate declared by the State Bank of India on the day prior to price bid opening. 
7.
Supply & Advance Notice


Mode of transport shall be through road only.

Immediately on dispatch, Supplier shall send advance information of dispatch particulars, by way of fax message to the following, giving details of Transport, LR no. its date, Invoice No., Date & value, No. of cases, gross weight, contents, etc. to M/s. Fluid Control Research Institute, Kanjikode west, Palakkad, Kerala, India – 678 623, Phone: 91 0491 2566120, 2566206 Fax No. 91 0491 2566326.

Supplier shall ensure that transmission of dispatch documents are arranged in accordance with the contract terms. In case of delay in clearance due to non-availability of documents shall be the responsibility of supplier & will be liable to bear expenses incurred on account of demurrage, wharfage etc.
8.
Preparation of Despatch Documents

All documents including LR, packing-list, Invoice etc. shall be in English. LR Invoice and packing list specifically must show, Mark & No., contents, case wise, consignee, final destination and all other particulars. The packing list must also show the actual contents in each case, net & gross weights and dimension with number of packages. The invoice must show item wise price break –up.

      One set of Despatch Documents should include the following documents.

i) LR (original)

ii) Invoice in Triplicate

iii) Packing List in Triplicate

iv) Manufactures test certificates/inspection note, warranty to Quality Certificates and any other document as specified in Purchase order
9.
Shipping (For Foreign Bidders)

Equipment packing 

      Equipment packing shall be strong and sturdy. Don’t frail the packing that may 
cause to       

      damage the equipment when loading/unloading, pushing and crane lifting 
etc. supplier is 
      responsible for any damages occurred while shipping the equipment. All packaging shall be      

      done so as to minimize volume and weight as much as possible  without  jeopardizing   the    

      safety of the material. All packing materials shall be new and shall be of  packer’s standard    

      for export shipments. Fragile articles should have special packing  materials  depending  on 
      type of materials.

Surface of equipment shall be thoroughly cleaned, freed from rust and grease and applied with sufficient coats of corrosion resistant paint. Surface preparation shall be carried out by shot blasting to SP-6 in accordance with “Steel Structures Painting Council – Visual Standard SSPC-IS-1”. Manufacturer shall indicate the type of corrosion resistant paint used, in the drawings submitted for approval. Sealant lines and cavities of the valve shall be filled with sealant before shipment. 

All mechanical and electrical equipment and other heavy articles should be securely fastened to the bottom of the case, to avoid damage.

All packages requiring handling by crane should have sufficient space at appropriate place to put sling of suitable dia (strength). Irons/steels angle should be provided at the place where sling markings are made to avoid damage to package/equipments while lifting.

Attachments and spare parts of equipments and all small pieces shall be packed separately in wooden cases with adequate protection inside the case and sent along with main equipment. Each item shall be tagged so as to identify it with the main equipment and part number and reference number shall be indicated.

All protrusions shall be suitably protected and openings shall be blocked by wooden/steel covers. All threaded fittings and pipes should be greased and provided with plastic caps

Wherever required equipments/materials shall be packed in polythene bags and silica gel or similar dehydrating compound shall be put inside the bags.
Detailed case wise packing list in waterproof envelope shall be inserted in each package together with equipment/material. One copy of ‘Detailed Packing List’ shall be fastened outside of the package in waterproof envelope and covered by metal cover. In case of bigger dia pipes and large equipments, documents contained in the envelope shall be fastened inside a shell connection with an identifying arrow sign ‘Documents” applied with indelible paint.
10.
Marking on Equipment.

Following markings are required shall appear on three sides of each package with proper paint/indelible waterproof ink for air / sea transportation.  

Name, Address and trademark of Supplier
:


For 





: 
Fluid Control Research Institute.

Airport/Port of despatch 


: 

Airport/Port of destination


:

P.O.No. 




:

Item Description 



:

Net weight 




:

Gross weight 



:

Case No. 




:

(No. of total cases) 


:

Dimension 




: 
Order Number 



:

Equipment Size and Rating 


:

Tag Number 



:

Serial Number 



:


Body Material Designation (MSS-SP-25)
:

     Important

Most appropriate and suitable packing for economical air/sea freight applicability, and shipping documentation, flight/shipment invoice and AWB/Bill of Lading & other documents as per normal practice shall be enclosed. 
11.
Disposal of Shipping Documents


Sea Shipments

The supplier shall prepare the complete shipping documents in all respects including three original stamped copies of Bill of Lading and courier the same as under :

i) Three copies of original Bill of Lading with one non-negotiable copy of Bill of Lading along with three copies each of original (a) Invoice, (b) Packing List, and (c) all other documents as specified in L/C shall be forwarded / negotiated through Beneficiary’s Bank to L/C Opening / Issuing Bank.

ii) One set of non-negotiable shipping document as mentioned towards “M/s Fluid Control Research Institute Kanjikode west, Palakkad, Kerala, India – 678 623, Phone: (91) 491- 2566120, 2566206, Fax No. (91) 491-2566326” to facilitate in pre-assessment of Custom Duty & other necessary formalities at Indian Port before arrival of consignment for speedy clearance of same.

iii) A set of non-negotiable shipping document as mentioned towards “M/s Fluid Control Research Institute Kanjikode west, Palakkad, Kerala, India – 678 623, Phone: (91) 491- 2566120, 2566206, Fax No. (91) 491-2566326” for advance information, scrutiny of documents (discrepancy, if any) & co-ordination.
12.
Air Shipments

Supplier shall prepare complete shipping documents including three original stamped copies of MAWB/HAWB/AWB and courier the same as under: -

i) Three copies of original AWB with one copy of non-negotiable AWB along with three copies each of original (a) Invoice, (b) Packing List, and (c) all other documents as specified in L/C shall be forwarded / negotiated through Beneficiary’s Bank to L/C opening / Issuing Bank.

ii) One set of non-negotiable shipping documents towards “M/s Fluid Control Research Institute, Kanjikode west, Palakkad, Kerala, India – 678 623, Phone: (91) 491-2566120, 2566206, Fax No. (91) 491-2566326” to facilitate in pre-assessment of Custom Duty & other necessary formalities at Indian Port before arrival of consignment for speedy clearance of same.

iii) One set of non-negotiable shipping documents towards “M/sFluid Control Research Institute, Kanjikode west, Palakkad, Kerala, India – 678 623, Phone: (91) 491-2566120, 2566206, Fax No. (91) 491-2566326” for advance information, scrutiny of documents & co-ordination.

13.
Short Supply 

Supplier should thoroughly check all items in the packing before effecting shipment. If any item(s) are found short packed in sound boxes on examination at project site, Supplier shall be responsible to supply short packed items free of charge on receipt of advice from FCRI. Supplier shall also be responsible to bear the import duty levied by Indian Customs on such short packed items.
14.
Shipping Instruction (For Domestic bidders)


Marking 

Supplier shall dispatch the consignment in road transport worthy packing conforming to the prescribed current standard. Packing should withstand journey & ensuring the safety to en-route & also arrival of equipment at ultimate destination in good condition.

Following marking shall appear on packing on outer side:

Name, Address and trade mark of Supplier
: 


For 





:
Fluid Control Research Institute 

Origin of Equipment 


:

Equipment Destination


:


Consignee




:

Order No.




:

Item




:

Net Weight 




:


Gross Weight



:

Cases No.




:

No. of total cases 



: 




Dimension




:

Order Number 



:

Equipment Size and Rating 


:

Tag Number 



:

Serial Number 



:


Body Material Designation (MSS-SP-25)
:

15.
Dispute


Any dispute regarding the Tender/Purchase Order shall be deemed to have arisen in 
Palakkad and only competent court in Palakkad will have jurisdiction. 

16 Overruling Clause 


Not withstanding anything stated anywhere in this document, the Director FCRI has the 
power to revise/add/review/delete/modify any of the conditions/statements indicated 
therein
XI. Award of Contract

1.
Post Qualification 

In the absence of pre qualification, FCRI will determine to its satisfaction whether the lowest bidder is qualified to satisfactorily perform the contract. 

The determination criteria will be bidder’s financial, technical and production capabilities as well as such other information as FCRI deems necessary and appropriate. 

Affirmative determination will be a prerequisite for award of contract to the bidder. A negative determination will result in rejection of the bidder’s bid. 

2.
Award Criteria 

FCRI will award the contract to Bidder whose bid has been determined as responsive and has been determined to be the lowest evaluated bid, provided further that the Bidder is determined to be qualified to perform the contract satisfactorily. 

3.
Change in Quantities 

FCRI reserves the right at the time of award of ORDER to increase or decrease by upto 15% the quantity of EQUIPMENT/Item specified in the Material Requisition, without any change in unit price or other terms and conditions. Variation beyond this limit will be subject to mutual agreement between FCRI and the Supplier. 

4.
Corrupt or Fraudulent Practices

“Corrupt practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of official in the procurement process or in contract execution. Any effort by a bidder to influence FCRI in any manner in respect of bid evaluation or award will result in the rejection of that bid.

“Fraudulent practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the detriment of FCRI, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive FCRI of the benefits of free and open competition;

FCRI will reject a proposal for award of it determines that the bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question. FCRI will declare a firm ineligible, either indefinitely on for a stated period of time, if at any time FCRI determines that the firm has engaged in corrupt or fraudulent practices in competing for or in executing a contract.  

XII Preambles To Schedule Of Quantities

1.
Rates quoted shall include all the operations, materials, etc., mentioned in the specifications of respective items of work, schedule of quantities, the preambles and required to complete the job.

2.
Rates quoted shall include all labour, materials, tools, plants, equipments and other 
sunderies etc, for workman like completion of work.

3.
Rates quoted shall be firm and shall not be subject to any variation due to increase in labour wages, cost of materials etc. or any other price variation whatsoever either by act of Government or otherwise whether during the stipulated period of execution or during extended period of completion if any.

4.
The works “as described”, “as specified”, “as shown”, “as directed” or         “as approved” shall mean as described in the specifications, schedule of quantities and other tender documents, as shown on the drawings and as directed or as approved by the Engineer in-charge.

5.
Your offer should remain valid for 6 months from the date of opening of tenders.

6.
For the purpose of quoting the rates, you may treat it as a case where there is no “C” or “D” form.

7.
The rate of taxes should be shown in the schedules and which should cover all taxes whatever form may be applicable and as prevailing on the date of quotation.

8.
The central excise duty tariff item and the normal duty thereof should be indicated separately. We are permitted Excise Duty Exemption with reference to Govt. Notification No. 10/97-Central Excise dated 1st March 1997.

9.
We are permitted Customs duty exemption with reference to Govt. Notification No. 51/96-Customs dated 23rd July 1996. 

10.
Any concession in excise duty/sales tax enjoyed by you should be clearly indicated in the covering letter.

11.
In case the components as  per our specification is not available, you may quote for the 
components of better specifications with clear indication of make, technical details etc.  
However such alternative components will be considered only on extraordinary 
circumstances.

12.
Liquidated damages for delay beyond the agreed delivery and commissioning schedule 
@0.5% per week subject to maximum of 10% of the total order value will be applicable.

13.
Failure to supply the materials as per delivery schedule is liable to result in cancellation 
of the order.

14.
Descriptive leaflets, brochures, drawings etc. showing the details should invariably be attached with your quotation.

15.
Declaration to the effect that the equipment supplied is original and is not reconditioned or refurbished items. 

Note: 
Preambles apply to all the sections of the schedule of quantities and tendered rates shall take into account all these provisions in addition to various provisions in other parts of the tender documents.
[image: image1.jpg]FLUID CONTROL RESEARCH lNSTITUTE
. e

TS .5 9001:2008 AN TA.T.
An 1SO 9001:2008 certified NABL accredited organisation
(res wewTe, A T TH A IR HA F N
(Under Govt. of India, Ministry of Heavy Industries & Public Enterprises)

MANDATE FORM FOR E-PAYMENT
1 “Name of the Beneficiary FLUID CONTROL RESEARCH INSTITUTE

2 Address Kanjikode (West),
Palakkad, Kerala - 678 623
il: feri@feriindia.com
wwiw.feriindia.com
Phone: +91 491 2566120/2566206
2569010 (Marketing)
Fax: +91491 2566326

3 PAN AAAAF0138K

4 Name of the Bank State Bank of India (SME Branch)
V&V Apartment Opp ITI, Kanjikode (W),
Palakkad 678 623.

Phone: +91 491 2566411/2566237

Email id : sbi.06640@sbi.co.in
5 Bank Account No 10258760349
6 Type of Account Current

7 Bank Branch RTGS IFSC Code SBIN0006640

8 Bank Branch Code 06640
9 9 Digit MICR Code of Branch 678002007
BANK CERTIFICATE

We confirm that the deteils given above are correct as per our records

S@ne

Place: ignatite & Stamp
Date: 57 yov 2016 of authorised bank offc

] com 1 o

“yh |





VOLUME – III of III
PRICE SCHEDULE 

FLUID CONTROL RESEARCH INSTITUTE

KANJIKODE WEST – 678 623, PALAKKAD, KERALA

(Under Ministry of Heavy Industries & Public Enterprises – Govt. of India)

Phone: (91) 491-2566120 / 2566206 / 2569009 Fax: 2566326

E-mail: purchase@fcriindia.com, fcri@vsnl.com Website: http://www.fcriindia.com
TENDER FORM

I/We hereby tender for the execution for…………………………………………………… ………………………………………………………………….of the item specified in the under written memorandum within the time specified in such memorandum at item rate entered in the schedule of quantities and in accordance in all respects with the specifications and instructions in writing referred to in Tender Documents.

MEMORANDUM

a)  General Description


:

b)  Estimated Cost



: 

c)  Earnest Money



:

d)  Time allowed for the work from 

:

     the date of written order to 

     commence.

Should this tender be accepted I/We hereby agree to abide by and fulfill all the terms and provisions of the General and Special conditions of contract so far as applicable or in default thereof to forfeit and pay to the Institute or its successors in office the sums of money mentioned in the said conditions. The sum of Rs……………………..(Rupees …………………………………………………………………………….) paid as Earnest Money is to be absolutely forefeited to the said Institute or its successors in office, without prejudice to any other rights or remedies of the said Institute or its successors in office, should I/We fail to satisfy the provisions contained in the relevant paragraphs of the tender forms.








SIGNATURE AND ADDRESS 








OF THE TENDERER

DATED
From






To

M/s. 






The Director








Fluid Control Research Institute







Kanjikode West – 678 623








Palakkad, Kerala.

Ref: 

Sub: Supply, Installation, Commissioning & Testing of New VFD for 187kW Pump-Motor including Removal of old Panel, etc.
l. No

Particulars


 
Amount

Remarks

Items as per Volume – III of III

Terms and conditions

We accept all terms and conditions listed in the Tender Documents.

Company’s Rubber stamp:

Place: 

Date: 
For Indigenous Supply 
	Sl. No.
	Item description
	Qty.
	Unit
	Rate

(Rs.)
	Amount

(Rs.)

	1.
	Supply, Installation, Commissioning & Testing of New VFD for 187kW Pump-Motor. 

(Complete items as detailed in page 4)

	1
	set
	
	

	2
	Accessories if any (Breakup to be given )


	1
	set
	
	

	3
	Ereation  and commissioning charges if any


	1
	No
	
	

	4
	Packing & Forwarding Charges


	
	

	5
	GST @ 5% against GST Exemption Certificate

	
	

	6
	Transportation charges up to FCRI

	
	

	7
	Insurance

	
	

	8
	Other Charges, if any

	
	

	9
	Buyback of existing VFD and Panel including removal of the same from the site


	
	

	Total Amount 
	


[image: image2.png]


















































































































PAGE  
16
Document No. PUR/FCRI/20046/VFD/2020-21

[image: image4.png]


